## E007 Spec
Product Specification Checklist
Single-phase voltage stabilizer |  |  |  | C | Conform
|  |  |  | O | Out of scope
MFR: |  |  |  | X | Non-conform
Product: |  |  |  | U | Compliance unknown
Specification: | E007/VS01.6
Review date:
Review by:
Performance Spec. Clause |  | PQS spec (latest) | Manufacturer comments | Conform | Comments | Actions | Manufacturer response
4.2 | Performance
4.2.1 | Mode of operation | Substantially maintenance free, No cooling fans
4.2.2 | Nominal input/output | 230 V; 50-60Hz (Extended required to tolerate wider range of input voltage)
4.2.3 | Input voltage fluctuations | @230 V; 50-60Hz Standard: Min = 173 V, Max = 278 V Extended: Min = 110 V, Max = 278 V
4.2.4 |  | Under/Overvoltage:
Electrical withstand:
Impulsive Transients:
Overload:
Short Circuit:
4.2.5 | Capacity rating | 1000 VA, 10 succesful start out of 10
4.2.6 | Input frequency fluctuations | +/- 3Hz for AC output +/- 5Hz for DC output Surface temperature 68°C or less.
4.2.7 | Output voltage accuracy | Maximum plus (+) 10% or minus (-) 15% of the nominal AC output voltages, or maximum plus (+) 5% or minus (-) 5% of the nominal DC output voltage, zero to full load, over the full input voltage regulation range specified by the manufacturer within which nominal output voltage, as specified in Section 4.2.2, can be supplied.
4.2.8 | Fuses | Fuses may not be used as a means of protection.
4.2.9 | Load power factor effect | AC voltage stabilizers shall be designed in such a manner that they have no effect on system PF. For SMPS, the device shall be equipped with a PF correction circuit to keep the magnitude of the power factor greater than or equal to 0.8.
4.2.10 | Waveform and distortion | An AC-output voltage stabilizer shall have an output voltage waveform with less than 3% total harmonic distortion when supplied with a sine wave input voltage.
4.3 | Materials and construction
4.3.1 | Corrosion resistance of enclosure | Legal Manufacturer to certify compliance: internal, external cabinet, lid, frame protected against corrosion as appropriate to EN ISO 6270-1 / ASTM D2247 / EN 13523-26 Determination of resistance to humidity – Continuous condensation, EN ISO 6270-2 / EN 13523-25 Determination of resistance to humidity - Procedure for exposing test specimens in condensation-water atmospheres, ISO 6272 / EN 13523-5 Impact resistance, and ISO 2049-2013
4.3.2 | Insulation | Insulation material Class 180 (H) or higher, as specified in IEC60085
4.3.3 | Restricted materials | The device shall comply with the Restrictions on Hazardous Materials Directive 2015/863 (RoHS 3). The device and its constituent components shall not contain lead, mercury, cadmium, hexavalent chromium, polybrominated biphenyls (PBB) or polybrominated biphenyl ethers (PBDE).
4.3.4 | Electrical safety | For AC voltage stabilizers, manufacturer to certify compliance with IEC 60335-1. For SMPS, manufacturer to certify compliance with IEC 61024-7.
4.3.5 | Electromagnetic compatibility | For AC voltage stabilizers, manufacturer to certify compliance with emissions requirement: IEC 61000-6-3; and Immunity requirement: IEC 61000-6-1. For SMPS, manufacturer to certify compliance with emissions requirement: IEC 61204-3 and CISPR 14-1; and Immunity requirement: CISPR 14-2.
4.3.6 | Robustness | Electrical: reliably operate under 100% (continuous) duty cycle. Mechanical: withstand vibration test IEC 60068-2-6, strength test IEC 60335-1 (Clause 21), thermal requirement IEC 60335-1 (clause 30).
4.3.7 | Protection against dust and water ingress | IP31 rating. If the solids ingress rating is not IP5X or better, any printed circuit board assembly shall be protected by conformal coating or potting.
4.3.8 | Markings | -The device enclosure shall be clearly marked to show the following: • Nominal input voltage and frequency. • Nominal output voltage and frequency. • kVA rating. • Grounding/Earthing terminal marking (for metal enclosures only) • Electric hazard warning -The top of the device enclosure shall also carry a waterproof label carrying the following user information in minimum 18-point lettering and in the language requested in the order: • “Voltage stabilizer for compression cycle, electric-gas absorption cycle and thermoelectric refrigerators and freezers.” • “DO NOT connect more than one appliance.”
4.3.9 | Efficiency | For SMPS devices, the operating efficiency shall be more than 90% at full rated load.
4.4 | Environmental Requirements
4.4.1 | Ambient temperature range during transport, storage and use | -30℃ to +70℃ when the product is inactive -5℃ to +43℃ during use
4.4.2 | Ambient humidity range during transport, storage and use | 5% to 95%RH, non-condensing
4.5 | Physical Characteristics
4.5.1 | Overall dimensions | No restriction
4.5.2 | Weight | No restriction
4.6 | Interface requirements
4.6.1 | Compatibility with electronic circuits | Vaccine refrigerators and freezers may contain non-adjustable electronic thermostats and electronic thermometers. The voltage stabilizer must not allow supply disruptions and/or voltage fluctuations which could damage such components to pass through to the refrigerator or freezer.
4.6.2 | Power lead | -Power lead with a sealed-on plug -The power lead must >= 1.5 meters. Both plug and output socket mounted on the device must be compatible with electricity socket standard in country where equipment is to be installed
4.6.3 | Power output | There shall be only one power outlet on the protection device. Devices with two or more outlets are not allowed. The outlet on standalone ac voltage stabilizers shall be compatible with the electricity socket standard in the country where the equipment is to be installed and shall include a protective earth connection. The output connection for standalone SMPS shall not be the same output socket used for AC applications. Protective earthing connections are also required.
4.7 | Human factors
4.7.1 | Generally | The device shall be designed for use by untrained personnel, in accordance with the general principles laid out in ISO 20282-1. In particular, indicator lights and lights labelling must be designed so that interpretation is not confusing for color blind users.
4.7.2 | Control panel | The device shall incorporate an LED that conveys when the input voltage is within the ranges specified in Clause 4.2.3. Voltmeters or indicator lamps should be positioned on the front or top of the unit.
4.8 | Warranty
The product is to be covered by a two year replacement warranty in the event of any component failure arising from defective design, materials or workmanship.
4.9 | Servicing provision
The product is to be designed to achieve a maintenance-free life of not less than 10 years, apart from occasional cleaning.
4.10 | Spare parts
The legal manufacturer or reseller shall provide a list of recommended spare parts as part of the instruction manual, referencing local parts as much as possible. These spare parts shall be made available for purchase at the time of device procurement. The legal manufacturer or reseller shall make anti-static wrist bands or other tools available to technicians to protect electronics under repair from electrostatic discharges.
4.11 | Disposal and recylcing
The manufacturer is to provide information to the buyer on the hazardous materials contained within the system and suggestions for resource recovery/recycling and/or environmentally safe disposal. For the European Union WEEE compliance in accordance with European Union Directive 2012/19/EU is mandatory. Test certification in compliance to IEC 62321-8 is also acceptable.
4.12 | Instructions
User and maintenance instructions are required to be available in Arabic, Mandarin Chinese, English, French, Russian and Spanish. The instructions are to be written for users and repair technicians and are to cover the following topics: • installation procedures; • interpretation of indicator lamps or LEDs; • reconnection instructions if applicable; • protection against electrostatic discharge and use of anti-static tools and/or or techniques; • routine maintenance tasks; • diagnostic and repair procedures; • itemized list of spare parts including part numbers; • end-of-life resource recovery and recycling procedures
5 | Packaging
Materials used for packaging the finished product are to be free of ozone- depleting compounds as defined in the Montreal Protocol. The general specification of shipping containers will be subject to agreement with the individual procurement agencies.
Step 4: Take a three quarter view digital photograph of each sample. A digital image should be provided for attachment to the PQS report. Take any other photographs needed to illustrate features of the product in the report.

## E007 Protocol
Verification Protocol Checklist
Single-phase voltage stabilizer |  |  |  | C | Conform
|  |  |  | O | Out of scope
MFR: |  |  |  | X | Non-conform
Product: |  |  |  | U | Compliance unknown
Protocol: | E007/VS01-VP.6
Review date:
Review by:
Protocol test |  | Protocol acceptance criteria (latest) | Manufacturer comments | Conform | Comments | Actions | Manufacturer reponse
5.4.4 | Vibration test | (Test 2)
-No damage to circuit boards or their mountings and the unit must function normally -light damage to packaging
5.4.5 | Impulsive transient protection test | (Test 3)
- No component failures (mechanical or electrical) - No component damage or evidence of arc flash between conductors and/or components - For AC voltage stabilizers residual voltage must be less than 400 V for 120 V / 50-60 Hz devices and 750 V for 230 V / 50-60 Hz devices. For SMPS, the residual voltage shall be no greater than three times the desired output and shall return to the set output voltage within two milliseconds.
5.4.6 | Electrical withstand test | (Test 4)
- No component failure or damage (mechanical or electrical) - Surface temperature of standalone stabilizers limited to the lesser of 68°C and the operating temperature limit of the enclosure.
5.4.7 | Voltage regulation range | (Test 5)
- Input range: Input voltage regulation range as specified by the manufacturer. - Output range: For AC voltage stabilizers, (+) 10% maximum or (-) 15% maximum over the full input voltage regulation range. For SMPS, (+) 5% maximum or (-) 5% maximum over the full input voltage regulation range. - For SMPS, the operating efficiency shall be 90% or greater when loaded at 100% of rated capacity.
5.4.8 | Frequency cut-off range | (Test 6)
- Input: Note the frequency at which the device cuts off and no longer provides output power. Note the time taken from frequency change to any cut-off of output voltage. - Output: For AC voltage stabilizers, no frequency less than 47 Hz and greater than 63 Hz is detected - Output is automatically restored when frequency is adjusted back in range after an optional delay of three to six minutes.
5.4.9 | High load starting | (Test 7)
Ten out of ten successful starts.
5.4.10 | Endurance test | (Test 8)
- No component failures (mechanical or electrical). - Surface temperature of standalone stabilizers limited to the lesser of 68°C. - The change in the output voltage should be within plus (+) 10% and minus (-) 15% of the nominal output voltage for AC voltage stabilizers when the input frequency is varied between 47Hz and 63Hz, and within plus (+) and minus (-) 5% for SMPS when the input frequency is varied between 45 Hz and 65 Hz.
5.4.11 | High/low voltage cut-off test | (Test 9)
The over/under-voltage protection cut-out must operate whenever the supply voltage is outside the applicable input voltage regulation range specified by the manufacturer by cutting the output voltage to zero. When the supply voltage is restored to a value within the applicable input voltage regulation range, the nominal output supply must be restored automatically after a delay of three to six minutes. Report the cut-out/cut-in voltage thresholds and the cut-in timings.
5.4.12 | Overload and short-circuit protection test | (Test 10)
1) The voltage stabilizer output voltage cuts out within 120 seconds when connected to a load equal to 150% the rated capacity. 2) The voltage stabilizer output voltage cuts out within 10 seconds when connected to a load equal to 720% the rated capacity. 3) The voltage stabilizer output voltage cuts out within 100 milliseconds when subjected to a simulated short circuit. 4) A period of 3 to 6 minutes need to elapse before an automatic reconnect device resets the overload disconnect mechanism or before the output voltage is automatically restored.
5.4.13 | IP rating test | (Test 11)
-IP31 test passed