## Spec
E007 Submission to PQS for approval: Single-phase voltage protection for ac and dc powered refrigerators and freezers
| Compliance with PQS specification: | E007/VS01.6 | Brand & Model:
| As shown by testing in accordance with PQS verification protocol: | E007/VS01-VP.6
Instructions in [square brackets] are for your guidance. Please delete these instructions and replace with evidence e.g. a precise reference (including page and section numbers) showing compliance with that particular PQS specification requirement. In general a "pass" or "complies" statement alone is not acceptable - evidence for compliance must be provided.
One document may provide evidence for several clause requirements. Please carefully reference the sub-sections of any such document so that it is clear that the clause requirement has been met. This will help speed the pre-qualification process.
Greyed-out cells are for information and do not require a response.
NOTE: If it is not clear or doubtful whether a requirement has been met, then this is a non-compliance and pre-qualification might be delayed.
| Please also complete the VP sheet. |  | REVIEWER’S SUMMARY: |  | REVIEWER’S SUMMARY: |  | REVIEWER’S SUMMARY:
Section 7. | Product dossier | Applicant's submission | Reviewer's remarks [Name & Date] | Applicants response [Name & Date] | Reviewer's remarks [Name & Date] | Applicants response [Name & Date] | Reviewer's remarks [Name & Date]
The legal manufacturer or reseller is to provide WHO with a pre-qualification dossier containing the following:
| Dossier examination fee in US dollars. | [Please arrange payment with WHO PQS.]
| General information about the legal manufacturer, including name and address. | [Please state.]
| Unique identification reference for the device type. | [Please state.]
| Full specifications of the device being offered, covering all the requirements set out in this document, including details of device marking and traceability. | [Please list the document(s provided in the submission for pre-qualification).]
| Full specification of the components used, including individual temperature ratings. | [Please list the document(s provided in the submission for pre-qualification).]
| Internal circuit diagram. | [Please refer to a document showing circuit diagram of the device.
| Photographs of the device clearly showing all sides of the device, including indicator lights and device identification labelling. | [Please refer to a document showing good quality photos. NOTE that photos are useful to help show compliance to particular clauses in the PQS Specification.]
| Certified photocopies of all type-approvals obtained for the device, including conformity assessment (e.g., CE, UL) marking and the like. If the certifications are not from an independent test lab, then the legal manufacturer shall provide a technical construction file that demonstrates conformity. | [Please refer to certified copies of all type approvals.]
| Certified photocopies of the legal manufacturer’s ISO 9001 quality system certification. | [Please refer to a document.]
| Certified photocopies of the Applicant's (if different from the legal manufacturer) ISO 9001 quality system certification. | [If applicable, please refer to a document.]
| Certified photocopies of the legal manufacturer’s ISO 14001 certification, EMAS registration or registration with an equivalent environmental audit scheme. Conformity with an environmental audit scheme is not mandatory; however, preference will be given to legal manufacturer who are able to demonstrate compliance with good environmental practice. | [Please refer to a document.]
| Certified photocopies of the testing laboratory’s ISO/IEC 17025 certification. | [Please refer to a document.]
| Laboratory test report(s) proving conformity with E007/VS01-VP.6. | [Please refer to a test report where the logger has been tested in accordance with PQS verification protocol WHO/PQS/E006/VS01-VP.6.]
| Details of the legal manufacturer’s internal Acceptable Quality Level (AQL) sampling procedures in respect of ISO 3951 and ISO 2859 or other internally recognized AQL standards. | [Please refer to a document.]
| Indicative cost of the device per unit, EXW (Incoterms 2020). | [Please state or refer to a document.]
Section 4. | Requirements
4.1 | General
A voltage stabilizer is designed to reduce fluctuations in input AC voltage and frequency, and to thereby ensure a stable electricity supply for refrigerators and freezers in environments without reliable, safe power. A switched mode power supply (SMPS) serves a similar purpose but converts AC to DC power for a DC-powered appliance. Both types of devices shall be compatible with compression cycle, electric-gas absorption cycle, Stirling, and thermoelectric equipment.
4.2 | Performance
4.2.1 | Mode of operation
| Both electronic and tap-changing technologies may be offered, but the device shall be substantially maintenance-free. AC-to-AC voltage stabilizers and SMPS that incorporate cooling fans are not acceptable because of the maintenance issues involved in keeping the airways clear. Devices that incorporate a SMPS to convert voltage and current from an AC source to a DC load are permitted. | [Please state type of device being offered and if any fans are used.]
4.2.2 | Nominal input and output voltage and frequency
| The device shall provide one or more of the following output voltage and frequency combinations when connected to an electric supply with one or more of the following nominal supply frequencies and voltage ranges. All devices shall operate with rated frequencies of 50-60 Hz. No devices are allowed that operate at only 50 or 60 Hz. Note that the “230/50-60: Extended” type is required to correct a wider range of input voltages (see Clause 4.2.3). This type is recommended for countries with wider input voltage fluctuations. Devices capable of operating at both 120 V and 230 V, 50-60 Hz nominal inputs are allowed, but verification testing shall be conducted at both these inputs for all tests. | [Please state the nominal input and output voltage and frequency of the product.]
4.2.3 | Input voltage fluctuations
| The device shall continue supplying acceptable output voltage as specified in Clause 4.2.7 within the following ranges of input voltage fluctuation. | [Please state the input voltage range of the product.]
4.2.4 | Voltage Protection
Under or Over-voltage:
| Overvoltage is most likely to cause rapid damage and should be removed as fast as practicable. The device output shall be isolated (i.e. switched to 0 volt) at the limits of the range at which its output is maintained within the regulation range as specified in Clause 4.2.7. While a response time is not specified, the intent is that stabilizers prevent damage to loads, which may be robust motors, or may include more sensitive electronic power supplies. | [Please refer to document or test report.]
| When the input voltage is restored to a value within the applicable input voltage regulation range as specified by the legal manufacturer, the AC or DC output supply shall be restored automatically after a delay of three to six minutes. This delay requirement may be waived if the legal manufacturer or reseller of an integrated or dedicated voltage stabilizer or SMPS demonstrates via evidence and written explanation that a delay is unnecessary for the appliance it is intended to protect. | [Please refer to document or test report.]
Electrical withstand:
| The device shall be able to withstand (i.e. without suffering any form of electrical or mechanical damage or failure) the ranges of continuous input voltage levels. | [Please refer to document or test report.]
| When exposed to voltages over the ranges in the table above, the surface temperature of a standalone stabilizer or SMPS tested in a 43°C ambient shall be limited to the lesser of 68°C and the operating temperature limit of the enclosure material. The first limit is to prevent skin burns to users and the second limit is to ensure enclosure integrity. For integrated and dedicated stabilizers or SMPS, the exterior surfaces of the appliance containing the stabilizer shall likewise respect the same limits, and the temperature of any internal enclosures must stay below the operating temperature limit of the enclosure material. | [Please refer to document or test report showing maximum surface temperature of the stabilizer.]
| For SMPS, also a dielectric strength test: • I/P-O/P (Input to Output): 1.5 kV ac / 1 min • I/P-F/G (Input to Protective Earth or “Ground”): 1.5 kV ac / 1 min • O/P-F/G (Output to Protective Earth or “Ground”): 0.5 kV dc / 1 min Note: The actual voltage range that the device can continuously withstand may be larger than the minimum voltage range specified above. | [For SMPS devices, please refer to document or test report showing compliance.]
Impulsive transients:
| The device shall be equipped with an impulsive transient suppression system capable of protecting the system from impulsive transients as described in IEC 61000-4-5. The device shall continue operating without any form of mechanical or electrical failure, damage, or arc flash between conductors and/or components. The device shall be tested to Installation Class 4: • A single impulsive transient of ±4 kV applied line-to-neutral, with a source impedance of 2 ohms. • Multiple impulsive transients of ±2 kV applied line-to-neutral, with a source impedance of 2 ohms. • Multiple impulsive transients of ±4 kV applied line-to-ground, with a source impedance of 12 ohms. • Multiple impulsive transients of ±4 kV applied neutral-to-ground, with a source impedance of 12 ohms. | [Please refer to test report showing impulse transients.]
| All residual voltage impulsive transients, after passing through the voltage stabilizer and onto the load under full boost condition for ac stabilizers, shall have peak amplitudes less than the following during the ±2 kV line-to-neutral test: Type Maximum residual voltage 120/50-60 400 V peak or below 230/50-60 750 V peak or below SMPS No greater than 3 times the set output voltage and return to the set output voltage within 2 milliseconds | [Please refer to test report showing maximum residual voltage.]
Overload:
| The device shall disconnect its output within the following disconnect times when connected to a load that exceeds the rated continuous output current capacity of the device by the corresponding overload percentages. The voltage stabilizer shall remain undamaged. 150% of rated capacity - 120 seconds 720% of rated capacity - 10 seconds Note: This is an adapted version of similar guidance according to IEC 60947-4-1 Class 10A overload breaker tripping characteristics. | [Please refer to document or test report showing disconnect within the required timeframe.]
| It shall be possible to reconnect manually or automatically to supply power when overload conditions less severe than a short circuit have been resolved. For automatic reconnection functionality, a delay of three to six minutes shall elapse between disconnection from supply power and automatic reconnection. Dedicated stabilizers can be exempted from this disconnect requirement, provided that the legal manufacturer can demonstrate that the device contains safeguards to prevent overloading the dedicated stabilizer in the event of a malfunction or operation outside the designed operating environment. | [Please state if reconnect is manual or automatic. If automatic, please refer to document or test report showing reconnect time delay.]
Short Circuit:
| For AC voltage stabilizers and SMPS, “short circuit” is defined as a load current greater than or equal to 1000% of the rated load current. The device shall disconnect its output within 100 msec in the event of a short circuit occurring at the output of the device, with instantaneous tripping current characteristics corresponding to Type C circuit protective devices as stipulated in IEC 60898-1. | [Please refer to document or test report showing a disconnect within 100ms of a short circuit event on the output.]
| It shall be possible to reconnect automatically or manually via the device to supply power when the short circuit has been resolved. Unplugging the device and plugging it back in is not an acceptable means of manually reconnecting for standalone stabilizers. Unplugging the appliance is an acceptable means of reconnecting for integrated and dedicated stabilizers because clearing a short circuit likely requires servicing the appliance, which is only safely accomplished by unplugging from mains. For automatic reconnection functionality, a delay of three to six minutes shall elapse between disconnection from supply power and automatic reconnection. Circuit breakers either on input side or the output side are acceptable. This delay requirement may be waived if the legal manufacturer of the voltage stabilizer or SMPS demonstrates via evidence and written explanation that a delay is unnecessary for the appliance it is intended to protect. | [Please state if the device automatically resets or whether it needs to be manually reset.]
4.2.5 | Capacity rating
| Minimum continuous capacity ratings are specified for standalone AC and DC output devices. No minimum rating is specified for integrated and dedicated devices, and this is left to the legal manufacturer to decide what rating best suits the application. The voltage stabilizer shall be able to provide the fully rated load in 10 out of 10 simulated compressor start events. | [Please state the capacity rating of the device and refer to document or test report showing 10 out 10 simulated compressor starts.]
4.2.6 | Input frequency fluctuations
| For AC devices, the device shall tolerate input frequency fluctuations between 47 and 63 Hz. The device shall cut off its output when the input frequency is less than 47 Hz or greater than 63 Hz unless it is of a type that can have a different output frequency than input frequency, in which case no frequency outside the range of 47-63 Hz should be detected at the output. | [Please state the output frequency of the stabilizer.]
| For SMPS, the device shall tolerate input frequency fluctuations between 45 and 65 Hz. Wider ranges are acceptable. The device shall cut off when the frequency is outside the legal manufacturer’s specified frequency range. | [For SMPS devices, state the input frequency range for the device.]
| For all devices, the output shall be automatically restored with an optional delay of three to six minutes when the frequency returns within the acceptable range. | [Please refer to document or test report showing output restored with a 3 to 6 minute delay.]
| When exposed to frequencies in the ranges above, the surface temperature of a standalone stabilizer or SMPS tested in a 43°C ambient shall be limited to the lesser of 68°C and the operating temperature limit of the enclosure material. The first limit is to prevent skin burns to users and the second limit is to ensure enclosure integrity. For integrated and dedicated stabilizers or SMPS, the exterior surfaces of the appliance containing the stabilizer shall likewise respect the same limits, and the temperature of any internal enclosures must stay below the operating temperature limit of the enclosure material. | [Please refer to document or test report showing maximum surface temperature of the stabilizer.]
4.2.7 | Output voltage accuracy
| For AC devices, the output voltage shall remain between plus (+) 10% and minus (-) 15% of the nominal output voltage in the table in Clause 4.2.2, when loaded from zero to full load, over the full input voltage regulation range specified by the legal manufacturer within which nominal output voltage, can be supplied. | [Please refer to document or test report showing the output voltage within the acceptable range across the full input voltage range.]
| For SMPS, the output voltage shall remain between plus (+) or minus (-) 5% of one of the nominal output voltages set out in the table in Clause 4.2.2, when loaded from zero to full load, over the full input voltage regulation range specified by the legal manufacturer within which nominal output voltage, as specified in Clause 4.2.2, can be supplied. | [For SMPS, please refer to document or test report showing the output voltage within the acceptable range across the full input voltage range.]
| Dedicated voltage protection, both AC voltage stabilizers and SMPS, shall provide a way for test laboratories to measure the device’s output voltage. If the legal manufacturer feels that its design should be exempt from output protection testing requirements due to the nature of the design, it may provide design information and data to justify that claim. | For applicable products, please refer to document or test report showing compliance with this requirement.]
4.2.8 | Fuses
| Fuses may not be used as a means of protection because they require spare parts and enable protection to be defeated with improper fuses. | [Please state if the device uses fuses.]
4.2.9 | Load power factor effect
| AC voltage stabilizers shall be designed in such a manner that they have no effect on system power factor (PF). | [Please refer to document or test report verifying the unit's effect on system PF.]
| For SMPS, the device shall be equipped with a PF correction circuit to keep the magnitude of the power factor greater than or equal to 0.8. | [Please refer to document or test report showing system PF.]
4.2.10 | Waveform and distortion
| An AC-output voltage stabilizer shall have an output voltage waveform with less than 3% total harmonic distortion when supplied with a sine wave input voltage. | [Please refer to document or test report showing output voltage waveform distortion.]
4.3 | Materials and construction
4.3.1 | Corrosion resistance of the enclosure
| For standalone voltage stabilizers and SMPS, the legal manufacturer shall declare compliance that the external cabinet and frame are protected against corrosion as appropriate to EN ISO 6270-1 / ASTM D2247 / EN 13523-26: Determination of resistance to humidity – Part 1: Continuous condensation, EN ISO 6270-2 / EN 13523-25: Determination of resistance to humidity - Part 2: Procedure for exposing test specimens in condensation-water atmospheres, ISO 6272 / EN 13523-5: Impact resistance – external cabinet, and ISO 2409: 2013: Paints and varnishes – crosscut test (external cabinet). Evidence for compliance to this clause shall be demonstrated. For integrated and dedicated voltage stabilizers and SMPS, the hardware and any enclosure material shall comply with the required performance specifications of the appliance within which it is integrated. | [Please refer to documents or test reports showing compliance to this requirement.]
4.3.2 | Insulation materials
| Legal manufacturer to declare that electrical insulation materials used in device construction complies with Class 180 (H) or higher, as specified in IEC 60085. Evidence for compliance to this clause shall be demonstrated. | [Please refer to document or test report showing compliance to this requirement.]
4.3.3 | Restricted materials
| The device shall comply with the Restrictions on Hazardous Materials Directive 2015/863 (RoHS 3). The device and its constituent components shall not contain lead, mercury, cadmium, hexavalent chromium, polybrominated biphenyls (PBB) or polybrominated biphenyl ethers (PBDE). | [Please refer to document or test report showing compliance to this requirement.]
4.3.4 | Electrical safety
| For AC voltage stabilizers, the legal manufacturer shall declare compliance with IEC 60335-1. Evidence for compliance to this clause shall be demonstrated in the form of a report from an accredited laboratory. For SMPS, the legal manufacturer shall declare compliance with IEC 61024-7. Evidence for compliance to this clause shall be demonstrated. | [Please refer to test report showing compliance to this requirement.]
4.3.5 | Electromagnetic compatibility
| For AC voltage stabilizers, the legal manufacturer shall declare compliance with the requirements of the latest version of IEC 61000-6-1 for EMC immunity requirements and IEC 61000-6-3 for EMC emission requirements. Evidence for compliance to this clause shall be demonstrated. For SMPS, the legal manufacturer shall declare compliance with the requirements of the latest version of IEC 61204-3 and CISPR 14-1 for EMC emission requirements and CISPR 14-2 for EMC immunity requirements. Evidence for compliance to this clause shall be demonstrated. | [Please refer to test report showing compliance to this requirement.]
4.3.6 | Robustness
Electrical:
| The device shall reliably operate at 100% of rated continuous capacity. | [Please refer to test report showing compliance to this requirement.]
Mechanical:
| The device, when packaged in the legal manufacturer’s standard packaging material, shall withstand the vibration tests specified in IEC 60068-2-6. The device shall also withstand the mechanical strength tests specified in in IEC 60335-1 (Clause 21) and thermal requirements specified in IEC 60335-1 (Clause 30) without suffering mechanical damage or functional failure. | [Please refer to test report showing compliance to this requirement.]
4.3.7 | Protection against solids and water ingress
| Voltage stabilizers and SMPS may be installed in environments that are dusty or humid, and enclosures may need to exclude rodents. Standalone devices shall have enclosures with a minimum IP31 rating. If the solids ingress rating is not IP5X (dust protected) or better, any printed circuit board assembly shall be protected by conformal coating or potting. Devices intended to be integrated within appliances are not required to have an enclosure with a specific IP rating. However, if the combination of appliance enclosure and stabilizer enclosure does not achieve a solids ingress rating of IP5X or better, printed circuit board assemblies shall be protected by conformal coating or potting. Manufacturers should consider coating guidelines in IPC document IPC-HDBK-830. | [Please refer to test report showing compliance to this requirement.]
4.3.8 | Markings
For all standalone devices that are not part of the appliance design, the device enclosure shall be clearly marked to show the following: Note: These markings are not necessary for integrated or dedicated devices.
| • Nominal input voltage and frequency. | [Please refer to a photo of the label.]
| • Nominal output voltage and frequency. | [Please refer to a photo of the label.]
| • kVA rating. | [Please refer to a photo of the label.]
| • Grounding/Earthing terminal marking (for metal enclosures only) | [For metal enclosure, please refer to a photo of the label.]
| • Electric hazard warning | [Please refer to a photo of the label.]
The top of the device enclosure shall also carry a waterproof label carrying the following user information in minimum 18-point lettering and in the language requested in the order:
| • “Voltage stabilizer for compression cycle, electric-gas absorption cycle and thermoelectric refrigerators and freezers.” • “DO NOT connect more than one appliance.” | [Please refer to a photo of the label.]
| In case of metal enclosed devices, all grounding terminals on the enclosure shall be identified with symbol IEC 60417-5017. | [For metal enclosure, please refer to a photo of the label.]
4.3.9 | Efficiency
| For SMPS devices, the operating efficiency shall be more than 90% at full rated load. | [For SMPS devices, please refer to test report showing efficiency of product.]
4.4 | Environmental requirements
4.4.1 | Ambient temperature range during transport, storage, and use
| -30°C to +70°C when the device is inactive. | [Please demonstrate or provide evidence that all components can tolerate temperatures in the range of -30°C to +70°C during transportation and storage. (Such evidence could be combined with the sub-clause below.)]
| -5°C to +43°C during use. | [Please demonstrate or provide evidence that all components can function in the range of -5°C to +43°C during use. (Such evidence could be combined with the above sub-clause.)]
4.4.2 | Ambient humidity range during transport, storage, and use
| 5% to 95% RH, non-condensing. | [Please demonstrate or provide evidence that the device can tolerate humidities within the range of 5 to 95%RH during transport, storage and use.]
4.5 | Physical characteristics
4.5.1 | Overall dimensions
| No restrictions. | [No requirements.]
4.5.2 | Weight
| No restrictions. | [No requirements.]
4.6 | Interface requirements
4.6.1 | Compatibility with electronic circuits
| Vaccine refrigerators and freezers may contain non-adjustable electronic thermostats and electronic thermometers. The voltage stabilizer shall not allow supply disruptions and/or voltage fluctuations which could damage such components to pass through to the refrigerator or freezer. | [Please state how the product does not interfere with the electronic circuits of vaccine refrigerators and freezers.]
4.6.2 | Power lead
| Standalone stabilizers and SMPS must be supplied with a power lead with a sealed-on plug that is compatible with the electricity socket in the country where the equipment is to be installed, and shall have a protective earth (“ground”) connection. The power lead shall be at least 1.5 m in length. | [Please provide photos of the power lead confirming plug and length.]
| Integrated and dedicated stabilizers and SMPS shall have a protective earth (“ground”) connection, unless the appliance in which it is integrated has class II protection against electric shock as described in IEC 60335-1. | [For integrated and dedicated stabilizers and SMPS, please confirm grounding scheme.]
4.6.3 | Power output
| There shall be only one power outlet on the protection device. Devices with two or more outlets are not allowed. | [Please provide photos showing the power outlet.]
| The outlet on standalone ac voltage stabilizers shall be compatible with the electricity socket standard in the country where the equipment is to be installed and shall include a protective earth connection. | [Please provide photos showing the power outlet.]
| The output connection for standalone SMPS shall not be the same output socket used for AC applications. Protective earthing connections are also required. | [For SMPS, please provide photos showing the output power connections.]
4.7 | Human factors
4.7.1 | Generally
| The device shall be designed for use by untrained personnel, in accordance with the general principles laid out in ISO 20282-1. Indicator lights and labelling shall be designed so that interpretation shall not be confusing for color-blind users. | [Please describe compliance with this requirement.]
4.7.2 | Control panel
| Standalone devices shall incorporate an LED that indicates when the input voltage is within the ranges specified in Clause 4.2.3. Voltmeters or indicator lamps shall be positioned on the front or top of the unit. An indicator is not mandatory for integrated or dedicated voltage stabilizers. | [Please describe, provide photos, or refer to document that confirms compliance with this requirement.]
4.8 | Warranty
| The device is to be covered by a two-year replacement warranty in the event of any component failure arising from defective design, materials, or workmanship. If the voltage protection device is part of the appliance it is protecting (either integrated or dedicated), the voltage protection device shall be covered under the same warranty terms & conditions as the protected appliance. | [Please refer to manufacturer's warranty statement.]
4.9 | Servicing provision
| The device is to be designed to achieve a maintenance-free life of not less than 10 years, apart from occasional cleaning. For dedicated and integrated stabilizers, all components providing voltage stabilization or protection functions shall be provided in a modular design that is easily replaceable by a trained technician, and such modules shall be commercially available as spare parts. | [Please describe how device meets this requirement.]
4.10 | Spare parts
| The legal manufacturer or reseller shall provide a list of recommended spare parts as part of the instruction manual, referencing local parts as much as possible. These spare parts shall be made available for purchase at the time of device procurement. | [Please refer to document with recommended spare parts list.]
| The legal manufacturer or reseller shall make anti-static wrist bands or other tools available to technicians to protect electronics under repair from electrostatic discharges. | [Please state how anti-static wrist bands or other tools can be made available to technicians.]
4.11 | Disposal and recycling
| The legal manufacturer or reseller is to provide information to the buyer on the hazardous materials contained within the system and suggestions for resource recovery/recycling and/or environmentally safe disposal. For the European Union WEEE compliance in accordance with European Union Directive 2012/19/EU is mandatory. Test certification in compliance to IEC 62321-8 is also acceptable. | [Please refer to the User Manual Section or to a document explaining what hazardous materials are contained within the system and show suggestions for resource recovery/recycling and/or environmentally safe disposal. (For the European Union WEEE compliance in accordance with European Union Directive is mandatory.)
4.12 | Instructions
| User and maintenance instructions are required to be available in Arabic, Mandarin Chinese, English, French, Russian and Spanish. The instructions shall be written for users and repair technicians and are to cover the following topics: | [Please confirm the manual is available in the required languages.]
| • installation procedures. | [Pleaser refer to the User Manual Section that describes the installation procedures.]
| • interpretation of indicator lamps or LEDs. | [Pleaser refer to the User Manual Section that describes the interpretation of indicator lamps or LEDs.]
| • reconnection instructions if applicable. | [Please refer to the User Manual Section that describes the reconnection instructions.]
| • protection against electrostatic discharge and use of anti-static tools and/or or techniques. | [Please refer to the User Manual Section that describes how to protect against electrostatic discharge and use of anti-static tools and/or or techniques.]
| • routine maintenance tasks. | [Please refer to the User Manual Section that shows detailed maintenance tasks.]
| • diagnostic and repair procedures. | [Please refer to the User Manual Section that shows diagnostic and repair procedures.]
| • itemized list of spare parts including part numbers. | [Please refer to the User Manual Section that shows itemized list of spare parts including part numbers.]
| • end-of-life resource recovery and recycling procedures. | [Please refer to the User Manual Section that shows end-of-life resource recovery and recycling procedures.]
4.13 | Training
Printed user-operations and maintenance instructions specifically directed at the health
5. | centre staff shall be pictorial. All key information is to be summarized on a single
pictogram sheet that may be fixed onto the appliance. The sheet is to be sufficiently
| Not required. | [Although not required, please state if there is any training available (videos, online, etc.).]
4.13 | Verification
| In accordance with PQS Verification Protocol WHO/PQS/E007/VS01-VP.6. | [Please refer to the test report detailing results in accordance with WHO/PQS/E007/VS01-VP.6. and see "VP Sheet" in this submission template.]
5.0 | Packaging
| Materials used for packaging the finished device are to be free of ozone-depleting compounds as defined in the Montreal Protocol. The general specification of shipping containers will be subject to agreement with the individual procurement agencies. | [Please state how the packing meets this requirement and refer to recommendations for correct disposal in the user manual.]

## VP
E007 Submission to PQS for approval: Single-phase voltage protection for ac and dc powered refrigerators and freezers
| Compliance with PQS specification: | E007/VS01.6 | Brand & Model:
| As shown by testing in accordance with PQS verification protocol: | E007/VS01-VP.6
Instructions in [square brackets] are for your guidance. Please delete these instructions and replace with evidence or a precise reference (including page and section numbers) showing compliance with that particular PQS specification requirement. In general a "pass" or "complies" statement alone is not acceptable.
One document may provide evidence for several clause requirements. Please carefully reference the sub-sections of any such document so that it is clear that the clause requirement has been met. This will help speed the pre-qualification process.
Greyed-out cells do not require a response.
NOTE: If it is not clear or doubtful whether a requirement has been met, then this is a non-compliance and pre-qualification might be delayed.
Please ensure the Spec sheet is completed.
Section 7. | VP Clause | Applicant's submission | Assessor's remarks [Name & Date] | Applicants response [Name & Date] | Assessor's remarks [Name & Date] | Applicants response [Name & Date] | Assessor's remarks [Name & Date]
5.1 | Evidence of conformity assessment
| Devices shall carry the CE mark, UL mark and/or equivalent internationally accepted evidence of conformity assessment. The legal manufacturer or reseller shall confirm to which clauses the device conforms. Certifications from accredited tests labs are preferable. If conformity is self-declared, then a technical construction file shall be provided as part of the dossier to validate conformity. | [Please provide evidence of any conformity mark if the appliance has one.]
5.2 | Number of samples
| The legal manufacturer or reseller shall supply the testing laboratory with a full duplicate set of the Product Dossier already supplied to WHO PQS in accordance with the requirements of specification Clause 7. One sample of the device is required. If the device is available in more than one of the versions and voltage combinations described in specification Clause 4.2.2, one sample of each version shall be provided for complete testing. | [Please provide the testing laboratory a draft dossier for checking and amendment. This will help to ensure that the dossier is complete.]
5.3 | Condition of samples
| The legal manufacturer or reseller shall supply all samples to the testing laboratory in the final form to be supplied to the end-customer. In the case of stabilizers or SMPS meant to be integrated into/unto the body of another product but tested outside it (integrated stabilizers), the stabilizer or SMPS samples shall be supplied to the testing laboratory mounted on a sturdy testing chassis (if necessary) that will mimic as closely as possible the final mounting method and orientation of all stabilizer components in the final device to be supplied to the end customer. | [Please state the form in which the sample has been provided to the testing laboratory.]
5.4 | Test procedure
5.4.1 | Voltage and frequency
The specific tests listed below apply equally to each combination of stabilizer or SMPS type and rated input voltage/frequency. Tests 2 to Test 10 shall be conducted in numerical order. Relevant input voltage/frequencies are given in the format: 120/50-60 or 230/50-60. The input to the stabilizer should be variable from 0 V to the upper limit of the legal manufacturer specified continuous operating input voltage range, and shall be regulated to ±1.0% of the nominal voltage used in all tests below. If the device is designed to operate at both 120 and 230 V AC nominal inputs, Tests 2 to Test 10 shall be conducted in numerical order with conditions relevant to both nominal voltages tested at each step. All results shall be reported for each test at each nominal voltage.
5.4.2 | Loading
| Many of the tests listed below require voltage stabilizers to operate under load. The load or loads used should be adjustable to draw current at 20%, 50%, 100%, 150%, 720% and 1000% of full rated current at rated output voltage. The following load types are acceptable: • Motor / dynamometer: Based on the type of device being tested, connect an AC (120 volt / 50-60 Hz or 230 volt / 50-60 Hz single phase) capacitor start induction motor or DC motor (12, 24, 48 volt) to the output of the voltage stabilizer or SMPS. The motor shall be the nearest size equivalent to the rated capacity of the voltage stabilizer or SMPS. Connect the output from the motor to a dynamometer so that calibrated loads of 20%, 50%, and 100% capacity can be obtained. Use this same motor for the 150% load point if possible, and a different motor or different load for the 720% and 1000% load requirement, if necessary. Set the dynamometer to control for constant torque equivalent to these load levels at expected rated speed. Motors should have starting current at least five times greater than the full-load current to approximate compressor start currents. For example, if a motor has a full-load current of 4.5 A, its start current rating should be ≥ 22.5 A. | [Please state the type of load used for testing.]
| • Programmable electronic load: A programmable AC or DC electronic load (as applicable) may be used to simulate a compressor or other load. Set the load to use constant current mode and for AC stabilizers, set the load power factor (PF) to 0.8 lagging (inductive). If used in the high-load starting test, note that 500% load current is needed and that transient or “inrush” capability would be helpful. • Resistor load: Acceptable for the impulsive transient test where it may be preferred not to connect sensitive equipment to the device under test. • Internal load for dedicated stabilizers: When testing an appliance that contains a dedicated stabilizer, the appliance’s internal load may be used to simulate the 100% loading and starting conditions. Use conditions that create the maximum appliance load. For example, compressors shall be run with the appliance equilibrated at +43°C. Potential scenarios for integrated and dedicated stabilizers are discussed in Annex 1. Note the special loading requirements described in Test 7, the high-load starting test. | [This row to be combined with the above.]
5.4.3 | Test 1: Type examination
| The test report must clearly show that the requirements of each section and sub-section in the type examination are individually and clearly met. | [Please refer to the test report and see the specification sheet in this template where precise references to each specification requirements are required. (Test 1 requirements refer to many specification clause requirements. See E007/VS01.6.)]
5.4.4 | Test 2: Vibration test
| Securely strap the sample to a vibrating table. Conduct vibration tests following the procedure in IEC 60068-2-6: Test Fc as follows: − Frequency: 10-150-10 Hz − Amplitude: (mean to peak) 0.35 mm − Rate of change: approximately 1 octave per minute − Acceleration: limited to 2 g (cross-over at 37 Hz) − Direction: vertical − Endurance: 20 sweep cycles. There shall be no damage to circuit boards, or their mountings and the unit shall function normally. Light damage to the packaging is acceptable but extensive damage to the packaging is not acceptable – for example if the stabilizer is able to fall out. | [Please refer to the precise section in the test report showing vibration test and any test details]
5.4.5 | Test 3: Impulsive transient protection test
• Step 1: Connect an IEC 61000-4-5 surge generator to the input of the voltage stabilizer or SMPS. Set the supply input voltage to the minimum voltage within the input voltage regulation range, as specified by the legal manufacturer, plus 5 V. Set and note the input frequency within the 50-60 Hz range. Set the surge generator’s source impedance to 2 Ω. Check whether the stabilizer output voltage is within plus (+) 10% maximum and minus (-) 15% of the nominal output voltage.
| • Step 2: Superimpose one (1) 4 kV impulsive transient voltage with an 1,2/50 μs waveform applied line-to-neutral on the input of the voltage stabilizer. The impulse shall be positive in polarity and be applied at the positive peak (90 degrees) of the AC waveform. Measure the maximum residual (let through) voltage resulting from this impulsive transient on the line-to-neutral output for AC voltage stabilizers and positive-to-negative for SMPS. (Note: An appropriate sampling rate to accurately characterize this short duration impulsive transient event should be utilized for measurement equipment, where appropriate). Record the maximum residual voltage and measurement sampling rate used. | [Please refer to the precise section in the test report showing maximum residual voltage and measurement sampling rate used.]
| • Step 3: Based on IEC 61000-4-5, superimpose five positive and five negative 2 kV voltage impulses at each of the following waveform phases: 0°, 90°, 180°, 270° with surge impedance set to 2 Ω. The impulses shall have 1,2/50 μs waveform applied line-to-neutral on the input. Wait one minute between pulses. Measure the maximum residual (let through) voltage resulting from this impulsive transient on the line-to-neutral output for AC voltage stabilizers or the positive-to-negative output for SMPS. (Note: An appropriate sampling rate to accurately characterize this short duration impulsive transient event should be utilized for measurement equipment, where appropriate). Record the maximum residual voltage and measurement sampling rate used. | [Please refer to the precise section in the test report showing maximum residual voltage and measurement sampling rate used.]
| • Step 4: Change the source generator’s source impedance to 12 Ω. Superimpose five positive and five negative 4 kV voltage impulses at each of the following waveform peaks: 0°, 90°, 180°, 270°. The impulses shall have 1,2/50 μs waveform applied line-to-ground on the input. Wait one minute between pulses. Measure the maximum residual (let through) voltage resulting from this impulsive transient on the line-to-neutral output of the AC voltage stabilizer or positive-to-negative for SMPS. (Note: An appropriate sampling rate to accurately characterize this short duration impulsive transient event should be utilized for measurement equipment, where appropriate). Record the maximum residual voltage and measurement sampling rate used. | [Please refer to the precise section in the test report showing maximum residual voltage and measurement sampling rate used.]
| • Step 5: Continue with the source generator’s source impedance set to 12 Ω. Superimpose five positive and five negative 4 kV voltage impulses at each of the following waveform phases: 0°, 90°, 180°, 270°. The impulses shall have 1,2/50 μs waveform applied neutral-to-ground on the input. Wait one minute between pulses. Measure the maximum residual (let through) voltage resulting from this impulsive transient on the line-to-neutral output of the AC voltage stabilizers or positive-to-negative for SMPS. (Note: An appropriate sampling rate to accurately characterize this short duration impulsive transient event should be utilized for measurement equipment, where appropriate). Record the maximum residual voltage and measurement sampling rate used. | [Please refer to the precise section in the test report showing maximum residual voltage and measurement sampling rate used.]
5.4.6 | Test 4: Electrical withstand test
• Step 1: Prepare to measure surface temperatures as described below with an uncertainty of ±0.5°C.
• Step 2: Set and note the input frequency within the 50-60 Hz range.
| • Step 3: Carry out the tests below, with the specified supply input voltage being maintained for 120 minutes for each test. For each test below, note the surface temperature of the hottest surface of the device at the start and end of the test. For dedicated stabilizers, measure the temperature of the appliance’s exterior surfaces closest to the stabilizer components and the surfaces of any internal enclosure around the dedicated stabilizer. | [Please refer to the precise section in the test report showing no damage to the device as well as the surface temperature of the device while under test.]
| Additional dielectric test for SMPS: I/P-O/P (Input to Output): 1.5 kV AC / 1 min I/P-F/G (Input to Protective Earth or “Ground”): 1.5 kV AC / 1 min O/P-F/G (Output to Protective Earth or “Ground”): 0.5 kV DC / 1 min | [For SMPS, please refer to the precise section in the test report showing the dielectric test.]
5.4.7 | Test 5: Voltage regulation range test
• Step 1: Set the input frequency to 60 Hz. Prepare to measure input and output power for SMPS efficiency tests.
• Step 2: Carry out the following tests, with supply voltage being varied from 0 V to the legal manufacturer specified upper limit of the continuous operating voltage range in increments of 5 V, with each voltage step being maintained for 5 minutes. Also sweep the voltage in the downward direction near the low voltage cut-in/cut-out and the high-voltage cut-out/cut-in points to determine if they are different due to hysteresis.
| Test: 5.1 Voltage: 0 – Specified upper limit Frequency: 50 Hz Load: none | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
| Test: 5.2 Voltage: 0 – Specified upper limit Frequency: 50 Hz Load: 20% of rated capacity | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
| Test: 5.3 Voltage: 0 – Specified upper limit Frequency: 50 Hz Load: 50% of rated capacity | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
| Test: 5.4 Voltage: 0 – Specified upper limit Frequency: 50 Hz Load: 100% of rated capacity | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
| Test: 5.1 Voltage: 0 – Specified upper limit Frequency: 60 Hz Load: none | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
| Test: 5.2 Voltage: 0 – Specified upper limit Frequency: 60 Hz Load: 20% of rated capacity | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
| Test: 5.3 Voltage: 0 – Specified upper limit Frequency: 60 Hz Load: 50% of rated capacity | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
| Test: 5.4 Voltage: 0 – Specified upper limit Frequency: 60 Hz Load: 100% of rated capacity | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
Acceptance criteria:
| − Input range: Input voltage regulation range as specified by the legal manufacturer, which shall be equal to the range outlined in specification Clause 4.2.3 or extend beyond it in either or both directions. An input range beyond the legal manufacturer’s specifications is acceptable. Record the voltage and frequency at which the device cuts out and no longer corrects voltage at the lower and upper bounds of voltage correction range. These cut-out points may vary depending on load. For clarity, the following relationships shall be satisfied at the lower and upper bounds of the input range for each loading level: o Lower: (lower measured cut-out voltage) ≤ (lower measured cut-in voltage) ≤ (Legal manufacturer’s specified lower voltage bound) ≤ (lower voltage bound as outlined in specification Clause 4.2.3) o Upper: (upper voltage bound as outlined in specification Clause 4.2.3) ≤ (Legal manufacturer’s specified upper voltage bound) ≤ (upper measured cut-in voltage) ≤ (upper measured cut-out voltage) | [The test report should clearly show the input voltage range. A "pass" statement alone is not acceptable.]
| − Output range: For AC voltage stabilizers, 120 V or 230 V plus (+) 10% or minus (-) 15% over the full input voltage range between measured cut-out voltages. For SMPS, the nominal output plus (+) or minus (-) 5% of the nominal output voltage over the full input voltage range between measured cut-out voltages. | [The test report should clearly show the output voltage. A "pass" statement alone is not acceptable.]
| − For SMPS, the operating efficiency shall be 90% or greater when loaded at 100% of rated capacity. | [For SMPS devices, the test report should clearly show the efficiency of the SMPS. A "pass" statement alone is not acceptable.]
5.4.8 | Test 6: Frequency cut-off range test
• Step 1: Set the supply voltage to the rated voltage of the device.
• Step 2: Vary the frequency in increments of 0.5 Hz, with each frequency step being maintained for a minute or until the output is disconnected.
| Test: 6.1 Frequency of 50 Hz adjusted down to 46 Hz for ac-output stabilizers and 44 Hz for SMPS Voltage: rated voltage for ac-output stabilizers and 230 V for SMPS Load: 100% of rated kVA capacity | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
| Test: 6.2 Frequency of 60 Hz adjusted up to 64 Hz for ac-output stabilizers and 65 Hz for SMPS Voltage: rated voltage for ac-output stabilizers and 230 V for SMPS Load: 100% of rated kVA capacity | [Please refer to a precise section in the test report showing the recorded data in graphical or tabular form. A "pass" statement alone is not acceptable.]
Acceptance criteria:
| − Input: Note the frequency at which the device cuts off and no longer provides output power. Note the time taken from frequency change to any cut-off of output voltage. Verify compliance based on type of device and associated requirements as outlined in Clause 4.2.6 of the specification. | [The test report should clearly show the input frequency. A "pass" statement alone is not acceptable.]
| − Output: For AC voltage stabilizers, no frequency less than 47 Hz and greater than 63 Hz is detected. | [The test report should clearly show the output frequency. A "pass" statement alone is not acceptable.]
| − Output is automatically restored when frequency is adjusted back in range after an optional delay of three to six minutes. | [The test report should report the reconnection time of the device.]
5.4.9 | Test 7: High load starting test
• Step 1: Set the input frequency to 60 Hz.
• Step 2: Set the supply voltage to the minimum voltage within the measured input voltage regulation range (see Test 5), plus 5 V.
| • Step 3: For motor loads and dedicated stabilizers using motor or compressor loads, cold start the motor ten times. For other stabilizers and loads, apply voltage ten times and measure the stabilizer output voltage during the high-current transient. | [Please refer to a precise section in the test report showing the 10 successful starts.]
| • Step 4: Repeat Steps 2 and 3 with the power supply set to a frequency of 50 Hz. | [Please refer to a precise section in the test report showing the 10 successful starts.]
5.4.10 | Test 8: Endurance test
• Step 1: Prepare to measure surface temperature as described below with an uncertainty of ±0.5°C.
• Step 2: Set and maintain constant supply voltage at the rated voltage (230 V for SMPS) and vary frequency in four steps (as specified below). For each step below, note the surface temperature of the hottest surface of the device at the start and at the instant when frequency is returned to 50-60 Hz. For dedicated stabilizers, measure the temperature of the appliance’s exterior surfaces closest to the stabilizer components and the surfaces of any internal enclosure around the dedicated stabilizer.
For AC voltage stabilizers: − Provide frequency of 47 Hz for 10 minutes, then return to 50-60 Hz for 10 minutes. − Provide frequency of 48 Hz for 60 minutes, then return to 50-60 Hz for 10 minutes. − Provide frequency of 62 Hz for 60 minutes, then return to 50-60 Hz for 10 minutes. − Provide frequency of 63 Hz for 10 minutes, then return to 50-60 Hz.
For SMPS − Provide frequency of 45 Hz for 10 minutes, then return to 50-60 Hz for 10 minutes. − Provide frequency of 46 Hz for 60 minutes, then return to 50-60 Hz for 10 minutes. − Provide frequency of 64 Hz for 60 minutes, then return to 50-60 Hz for 10 minutes. − Provide frequency of 65 Hz for 10 minutes, then return to 50-60 Hz.
| • Step 3: Fix the input frequency to 50 or 60 Hz based on whichever end of the spectrum is shown to have the hottest surface temperatures from Step 2. Vary the supply voltage between the minimum in the measured input voltage regulation range (see Test 5), plus 10 volts, and the maximum (see Test 5) minus 10 volts, at a frequency of l0 cycles per minute. Continue the test including measuring temperatures for a minimum of 96 hours. Report any breakdowns. | [Please refer to a precise section in the test report or other document showing the temperature measurements. A "pass" statement alone is not acceptable.]
| • Step 4: Hold the supply voltage constant at the minimum value within the measured input voltage regulation range (see Test 5). On tap-changing stabilizers, this will be at an input voltage below the first tap change. Conduct this test for a further 12 hours and report any breakdowns. | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
| • Step 5: Hold the supply voltage constant at the maximum value within the measured input voltage regulation range (see Test 5) for a further 12 hours. Report any breakdowns. | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
5.4.11 | Test 9: High/low voltage cut-off test
• Step 1: Set and note the input frequency within the 50-60 Hz range.
• Step 2: Refer to the upper and lower limits of voltage regulation range and input voltage cut out that were established in Test 5 for the fully loaded case.
| • Step 3: Set the maximum voltage at which the under-voltage cut-out operates and maintain it for one minute. Then follow it with a period at nominal supply voltage (120/230 V) until the output voltage is restored. Record the time period between when nominal supply voltage is restored and when output voltage is restored. | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
| • Step 4: Maintain the minimum voltage at which the over-voltage cut-out operates for a period of one minute followed by a period at nominal supply voltage (120/230 V) until the output voltage is restored. Record the time period between when nominal supply voltage is restored and when output voltage is restored. | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
5.4.12 | Test 10: Overload and short-circuit protection test
• Step 1: Set the supply voltage at the nominal value (120 V or 230 V, using 230 V for SMPS). Set and note the input frequency within the 50-60 Hz range.
| • Step 2: Load the device to 150% the rated capacity of the device and record the time before the output voltage cuts out. | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
| • Step 3: Reset the device (manually or automatically) and record the time period elapsed between output voltage cut-out and when it is possible to reset the overload disconnect mechanism. | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
| • Step 4: Load the device to 720% of the rated capacity of the device and record the time before output voltage cuts out. | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
| • Step 5: Reset the device (manually or automatically) and record the time period elapsed between output voltage cut-out and when it is possible to reset the overload disconnect mechanism. | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
| • Step 6: Load the device to 1,000% the rated capacity (in output current) of the device for AC stabilizers and SMPS to simulate a short-circuited load and record the time before output voltage cuts out | [Please refer to a precise section in the test report or other document showing the recorded measurements. A "pass" statement alone is not acceptable.]
5.4.13 | Test 11: IP rating test to IEC 60529
| For integrated and dedicated voltage stabilizers or SMPS, the voltage protection device shall meet the requirements of the appliance within which it is integrated. For standalone voltage stabilizers and SMPS, obtain an independent test report from the legal manufacturer or reseller showing full conformity with IEC 60529: IP31 or better. | [Please refer to the precise section in the test report showing IP test and any test details]