## Spec
E007 Submission to PQS for approval: Three-phase voltage stabilizer for AC powered Walk-In Cold & Freezer Rooms |  |  | Brand & Model:
| Compliance with PQS specification: | E007/VS02.1
| As shown by testing in accordance with PQS verification protocol: | E007/VS02-VP.1
ASSESSOR’S SUMMARY:
Instructions in [square brackets] are for your guidance. Please delete these instructions and replace with evidence or a precise reference (including page and section numbers) showing compliance with that particular PQS specification requirement. In general a "pass" or "complies" statement alone is not acceptable.
One document may provide evidence for several clause requirements. Please carefully reference the sub-sections of any such document so that it is clear that the clause requirement has been met. This will help speed the pre-qualification process.
Greyed-out cells do not require a response.
NOTE: If it is not clear or doubtful whether a requirement has been met, then this is a non-compliance and pre-qualification might be delayed.
| Please also complete the VP sheet. |  | REVIEWER’S SUMMARY: |  | REVIEWER’S SUMMARY: |  | REVIEWER’S SUMMARY:
Section 8. | Product dossier | Applicant's submission | Reviewer's remarks [Name & Date] | Applicants response [Name & Date] | Reviewer's remarks [Name & Date] | Applicants response [Name & Date] | Reviewer's remarks [Name & Date]
The legal manufacturer or reseller is to provide WHO with a pre-qualification dossier containing the following:
| Dossier examination fee in US dollars. | [Please arrange payment with WHO PQS.]
| General information about the legal manufacturer, including name and address. | [Please state.]
| Unique identification reference for the for the product type. | [Please state.]
| Full specifications of the product being offered, covering all the requirements set out in this document, including details of product marking and traceability. | [Please list the document(s provided in the submission for pre-qualification).]
| Photographs of the product clearly showing all sides of the device, including indicator lights and product identification labeling. | [Please refer to document(s).]
| Certified copy of the legal manufacturer’s current ISO 9001 quality system certification. | [Please refer to a document.]
| Where relevant, certified photocopies of the legal manufacturer’s ISO 14001 certification, EMAS registration or registration with an equivalent environmental audit scheme. Conformity with an environmental audit scheme is not mandatory; however preference will be given to manufacturers who are able to demonstrate compliance with good environmental practice. | [Please refer to a document.]
| Certified photocopies of the testing laboratory’s ISO/IEC 17025 certification. | [Please refer to a document.]
| Where available, laboratory test report(s) proving conformity with the product specifications. | [Please refer to a test report where the product has been tested in accordance with PQS verification protocol WHO/PQS/E007/VS02-VP.1.]
| Indicative cost of the product per unit, EXW (Incoterms 2010). | [Please state or refer to a document.]
Section 4. | Requirements
4.1 | General
A three-phase voltage stabilizer is designed for use in Walk-in Cold/Freezer Rooms (WICRs/FRs) for stabilization and protection against voltage fluctuations, impulsive transients, surges and short circuits for compression refrigeration units associated electronic controls, amongst other factors. The stabilization may include short or prolonged under- or over-voltage ranges outside the limits prescribed in the performance clauses below. The device may be configured for star or delta connection in the various different national grid utility tensions in countries.
4.1.1 | Technology
| These shall be any of the following: Electronic Tap Changing / Servo-Mechanical / Solid State Electronic Tap Switching / Switch-mode power converters. (New and emerging technologies are allowed.) | [Please state the type of technology used in the voltage stabilizer.]
4.2 | Performance
4.2.1 | Mode of operation
| The device must be substantially maintenance-free, except for servo-mechanical types which are permitted periodic maintenance. Products that incorporate cooling fans are acceptable, but fans shall be thermostatically controlled to increase fan lifetime. All air inlets used for ventilation shall incorporate mechanisms such as, but not limited to, inlet protection cages that prevent the inlet from being blocked to the extent that it will affect device operation or lifetime. | [Please state how product is compliant.]
4.2.2 | Nominal input and output voltage and frequency
| A voltage stabilizer shall be characterized as one of the following types based on its rated nominal input and output voltages. The first type is for countries with nominal 120 V voltages. The second type may be optimized for 230 V operation, while the third type must support multiple voltage configurations. The purchaser shall specify the nominal supply voltage of the third type so that the manufacturer can optimize the product before delivery. Refer to the table in clause 4.2.2. | [Please state the voltages and frequencies for which the voltage stabilizer is available.]
4.2.3 | Input voltage fluctuations
| The device shall stabilize its output voltage to the nominal voltage specified in Clause 4.2.2, with tolerance as specified in Clause 4.2.7 when supplied with three-phase input voltage in the range applicable to its type, as shown in the table in clause 4.2.3. | [Please provide evidence that the device can stabilize the out voltage based on the specified input voltage fluctuations.]
4.2.4 | Voltage Protection
Under- or Over-voltage
| All three phases of the device output (neutral-phases and phase-phase), must simultaneously be isolated (i.e. switched to 0 volt) at the limits of the manufacturer specified input voltage regulation range, as specified in Clause 4.2.3. When the input voltage for each phase is restored to a value within the applicable input voltage regulation range as specified by the manufacturer, the output supply must be restored automatically for all three phases simultaneously after a delay predetermined by the manufacturer. (Note: This may vary according to the specific individual design specification). | [Please provide evidence that the device can switch off the output when the input voltage is outside the regulation range of the device, and can automatically restore the output when the input voltage is within the operating range of the device.]
Electrical withstand
| The device must be able to withstand the following minimum ranges of continuous input voltage levels for each phase, without suffering any form of electrical or mechanical damage or failure. When testing, the high withstand, voltage shall be applied in a way that it rises from “in range” (e.g. 230 V phase-to-neutral for a 230 V stabilizer) to the maximum level (e.g. 415 V) within 3 seconds. Note: The actual voltage ranges that the device is able to continuously withstand may be larger than the minimum voltage ranges specified. | [Please provide evidence of voltage withstand.]
Impulsive Transients
| The device must be equipped with an impulsive transient protection system capable of protecting each input phase to the following minimum specifications, allowing the device to continue operating after a maximum rated impulsive transient event on each individual input phase without any form of mechanical or electrical failure, damage or arc flash between conductors and/or components: | [Please provide evidence of impulse transient withstand.]
Phase Failure and Reversal
| The device must be able to detect a phase failure on one or more of the input phases and should isolate all the output phases (i.e. switch all output phases to 0 volt) in the event of such a failure. The device must also be able to detect incorrect phase sequencing or reversal and should isolate all the three output phases (i.e. switch all output phases to 0 volt) in the event such a fault is detected. | [Please provide evidence that the device can switch off the output when there is a phase failure of 1 or more input phases.]
| Output supply of the device must be automatically and simultaneously restored for all three phases (i.e. with no user intervention needed) within a predetermined delay period (manufacturers to state delay period with respect to their device design) after the phase failure or reversal has been corrected. (Manual resetting is an option.) | [Please provide evidence that the device can automatically restore the output when the phase failure has been corrected.]
Overload
| The device must disconnect from supply power within the following maximum disconnect time, when connected to a load that exceeds the maximum rated capacity of the device by the corresponding overload factor (rated capacity x overload factor). | [Please provide evidence of shutdown on load overload.]
| It must be possible to reconnect the phase inputs to supply power manually or automatically when the overload condition has been resolved, with the requirement that a minimum predetermined period should have elapsed since the disconnection from supply power. | [Please state whether the reconnect is automatic or manual.]
Short Circuit
| The device must disconnect all three phases from supply power within 100 ms in the event of a short circuit occurring downstream from the device, with instantaneous tripping current characteristics corresponding to Type C circuit protective devices as stipulated in IEC 60898-1. (Other acceptable international standards are an option.) | [Please provide evidence of shutdown on load short circuit.]
| Note: It must be possible to reconnect manually or automatically to mains power when the short circuit has been resolved, with the requirement that a minimum predetermined period should have elapsed since disconnection from mains power. | [Please state whether the reconnect is automatic or manual.]
4.2.5 | Capacity rating
| Capacity rating (kVA) shall match the total power consumption of the load, i.e. the WICR/FR, inclusive of all its accessories. The designed capacity shall meet both the inrush/startup current of the inductive load of the WICR/FR, as well as the peak current over the full voltage regulation range. Under fully rated load conditions there must be 10 successful compressor starts out of 10. | [Please state capacity of device and provide evidence of 10 out of 10 starts under full load condition.]
4.2.6 | Input frequency fluctuations
| The device must tolerate input frequency fluctuations up to ±3.0 Hz continuously, ±4.0 Hz up to an hour, ±5.0 Hz for 10 minutes (equal frequency fluctuation across all phases). This is an adapted version of similar guidance from EN60950 standards. | [Please provide evidence the device can tolerant frequency fluctuations.]
4.2.7 | Output voltage accuracy
Accuracy
| Maximum plus (+) 4% or minus (-) 4% or better of the nominal output voltages set out in the table in Clause 4.2.2, zero to full load, over the full input voltage regulation range specified by the manufacturer in accordance with Clause 4.2.3. This is to be tested in accordance with the EN60950 standards. | [Please provide evidence of output voltage accuracy.]
Phase Balancing
| Output voltage imbalance between the phases with the lowest and highest output voltages respectively, must never be more than 10 % of the average voltage value measured across all three-output phases. In the event that the phase imbalance cannot be contained within 10%, all three output phases should be isolated (i.e. all output phases switched to 0 volt). It is acceptable for this threshold to be customer adjustable, on condition that the default value is 10%. | [Please provide evidence of output shutdown on phase imbalance.]
4.2.8 | Efficiency
| Device efficiency must be greater than or equal to 92% at full load. | [Please provide evidence of efficiency of 92% or greater.]
4.2.9 | Stability
| Voltage regulation performance, as required in Clauses 4.2.3 – 4.2.7, must be stable for all power factors for the respective input voltages. | [Please provide evidence of stability for all power factors for the respective input voltages.]
4.2.10 | Harmonic distortion
| Manufacturer shall certify that the total harmonic distortion induced or allowed on each of the three output phases is less than 3%. | [Please provide evidence of harmonic distortion of 3% or less on all 3 output phases.]
4.2.11 | Bypass switch
| Manual bypass switch The device must be equipped with a fully rated manual bypass switch capable of fully bypassing (isolating) the voltage stabilizer and manually bypassed to connect the cold/freezer room directly to the mains power supply in the event of a stabilizer malfunction or failure. | [Please provide evidence of a manual bypass switch.]
4.2.12 | Insulation materials
| Manufacturer shall certify that electrical insulation materials used in device construction complies with Class 180 (H) or higher, as specified in IEC 60085. | [Please provide evidence device has an electrical insulation of IEC 60085 Class 180 (H) or higher.]
4.2.13 | Corrosion resistance of enclosure
| Manufacturer shall certify compliance that internal and external cabinet, lid and frame are protected against corrosion as appropriate to: ENISO6270-1/ ASTMD2247/EN13523-26 Determination of resistance to humidity–Part 1: Continuous condensation; ENISO6270-2/EN13523-25 Determination of resistance to humidity- Part 2: Procedure for exposing test specimens in condensation-water atmospheres; ISO6272/EN13523-5 Impact resistance–external cabinet; and ISO2409 Paints and varnishes–crosscut test (external cabinet). | [Please provide evidence of corrosion resistance.]
4.2.14 | Electrical safety
| Manufacturer shall certify compliance with IEC 60335-1. Component transformers shall comply with IEC 61558-1. The equipment shall comply with applicable safety codes and statutory regulations of the locality where the equipment is to be installed. The procurement agency of the equipment shall enquire whether the equipment specifications comply with the applicable safety codes and statutory regulations of the country/location where the equipment is to be installed. Reason: 1. Statutory regulations and codes differ for different countries 2. No standards have been developed in some developing countries | [Please provide evidence of electrical safety.]
4.2.15 | Electromagnetic compatibility
| To ensure product meets EMC emissions requirements, legal manufacturer must certify compliance to the latest version of IEC 61000-6-3. To ensure product meets EMC immunity requirements, legal manufacturer must certify compliance with the requirements of the latest version of IEC 61000-6-1. To ensure product meets EMC harmonic distortion requirements where appropriate, legal manufacturer must certify compliance with the requirements of the latest version of IEC 61000-3-2. | [Please provide evidence for Electromagnetic compatibility.]
4.2.16 | Robustness
| Electrical The device must reliably operate under a 100% (or continuous) duty cycle. | [Please provide evidence of electrical robustness.]
| Mechanical The device, when packaged in the manufacturer’s standard packaging material, must withstand the vibration tests specified in IEC60068-2-6 as well as the mechanical strength tests specified in IEC60950-1 (Clause 4.2) and thermal requirements specified in IEC60950-1 (Clause 4.5) without suffering mechanical damage or functional failure. (Any other international standard that closely matches the above is acceptable.) | [Please provide evidence of mechanical robustness to IEC specifications.]
4.2.17 | Protection against dust and water ingress
| Voltage stabilizers for cold or freezer room applications may be installed in environments that are dusty or humid. The design of the device should ensure that it is not damaged by dust penetration (e.g. conformal coating for circuit boards). The enclosure shall have a minimum ingress protection rating of IP21. | [Please provide evidence of IP21 compliance.]
4.2.18 | Markings
| The acceptable location (country) for data hosting and associated server storage shall be negotiated between the legal manufacturer or reseller and the employer at the time of procurement. If the employer prefers to host data within their country, the legal manufacturer or reseller should make efforts to support this approach. However, the ultimate responsibility for establishing secure, functional data hosting within a programme country is the responsibility of the employer unless otherwise negotiated with the legal manufacturer or reseller. | [Please provide evidence of compliance to required markings and labels.]
4.3 | Environmental requirements
4.3.1 | Ambient temperature ranges during transport, storage and use
| -30°C to +70°C when the product is inactive. -5°C to +43°C during use. | [Please demonstrate or provide evidence that all components can tolerate temperatures in the range of -30°C to +70°C during transportation and storage.]
4.3.2 | Ambient humidity range during transport, storage and use
| 5% to 95% RH, non-condensing. | [Please demonstrate or provide evidence that the device can tolerate humidities in the range of 0 to 95%RH during transportation, storage and use.]
4.3.3 | Audible noise level
| Less than 50dBA at one meter or compliance to ANSI/ASA S3.21-2004 (R 2009). If not to this standard, indicate the standard or noise level that the device conforms. | [Please state level of audible noise for the device.]
4.4 | Physical characteristics
4.4.1 | Overall dimensions
| No restrictions. | [Please state the dimensions for the voltage stabilizer.]
4.4.2 | Weight
| No restrictions. | [Please state the weight of the voltage stabilizer.]
4.5 | Interface requirements
4.5.1 | Compatibility with electronic circuits
| Cold or freezer rooms may contain non-adjustable electronic thermostats and electronic thermometers. The voltage stabilizer must not allow supply voltage fluctuations, which could damage such components, to pass through to the cold or freezer room controls. | [Please state how the device complies with this requirement.]
4.6 | Human factors
4.6.1 | General
| In accordance with the general principles laid out in ISO20282-1, the design of the device shall be easy to operate. In particular, indicator lights and indicator light labeling must be designed so that interpretation is not confusing for color blind users. | [Please state how the device complies with this requirement.]
4.6.2 | Control panel
| The device must incorporate full input and output voltage indicators per phase, in combination with status indicators that indicate when each phase’s input voltage is within the input voltage regulation range specified by the manufacturer within which nominal output voltage, as specified in Clause 4.2.2, can be guaranteed. Status indicators should also be included to indicate major faults such as under and over voltages, phase failures, phase reversals and phase imbalances. Displays and other status indicators must be positioned on the front or top of the unit. | [Please state how the device complies with this requirement.]
4.7 | Materials
4.7.1 | Restricted materials
| The product and its constituent components must not contain lead, mercury, cadmium, hexavalent chromium, poly brominated biphenyls (PBB) or poly brominated biphenyl ethers (PBDE). | [Please provide a RoHS report or equivalent.]
4.8 | Warranty
| The product is to be covered by a two-year replacement warranty in the event of any component failure arising from defective design, materials or workmanship. | [Please state or refer to a document showing the warranty with terms and definitions.]
4.9 | Servicing provision
| The product is to be designed to achieve a substantially maintenance-free life of not less than 10 years, apart from occasional cleaning and the replacement of user-accessible fuses, if any. | [Please explain how the device is designed to achieve a low-maintenance life apart from routine cleaning. The minimum operational lifetime of the device shall be at least 10 years.]
4.10 | Disposal and recycling
| The manufacturer is to provide information to the buyer on the hazardous materials contained within the system and suggestions for resource recovery/ recycling and/or environmentally safe disposal. For the European Union WEEE compliance in accordance with European Union Directive 2002/96/EC is mandatory. | [Please refer to a user manual Section or to a document explaining what hazardous materials are contained within the system and show suggestions for resource recovery/recycling and/or environmentally safe disposal. (For the European Union WEEE compliance in accordance with European Union Directive is mandatory.)]
4.11 | Instructions
User and maintenance instructions are required to be available in Arabic, Mandarin Chinese, English, French, Russian and Spanish. The instructions are to be written for users and repair technicians and are to cover the following topics:
| 1. General description of equipment | [Pleaser refer to the manual Section that contains the general description of equipment.]
| 2. Approved Technical Data Sheet | [Pleaser refer to the manual Section that contains the technical data of the device.]
| 3. Salient constructional features | [Pleaser refer to the user manual Section that shows the salient constructional features.]
| 4. Technical leaflets of fittings/ important parts | [Please refer to the manual Section that shows technical leaflets of fittings/ important parts.]
| 5. All drawings | [Please refer to the manual Section that contains the device drawings.]
| 6. Type and routine test certificates | [Please refer to the manual Section that contains the type and routine test certificates.]
| 7. Instructions to be followed on receipt of equipment at site and for storage | [Please refer to the manual Section that shows the instructions to be followed on receipt of equipment at site and for storage the type and routine test certificates.]
| 8. Instructions for foundation arrangement | [Please refer to the manual Section that shows the instructions for foundation arrangement.]
| 9. Installation procedures | [Please refer to the manual Section that shows the Installation procedures.]
| 10. Pre-commissioning checks | [Please refer to the manual Section that shows the pre-commissioning checks.]
| 11. Commissioning procedures | [Please refer to the manual Section that shows the commissioning procedures.]
| 12. Withdrawal arrangement/material handling instructions | [Please refer to the manual Section that shows the material handling instructions.]
| 13. Operation instructions | [Please refer to the manual Section that shows the operation instructions.]
| 14. Maintenance instructions | [Please refer to the manual Section that shows the maintenance instructions.]
| 15. Itemized list of spare parts including part numbers | [Please refer to the manual Section that contains the Itemized list of spare parts.]
| 16. Trouble-shooting | [Please refer to the manual Section that contains troubleshooting instructions.]
| 17. Safety instructions | [Please refer to the manual Section that contains safety instructions.]
| 18. End-of-life resource recovery and recycling procedures | [Please refer to the manual Section that contains recycling instructions.]
4.12 | Training
| Not required. | [Although not required, please state if there is any training (i.e. online videos, etc.).]
4.13 | Verification
| In accordance with PQS verification protocol E007/VS02-VP.1 | [Please refer to the WHO/PQS/E007/VS02-VP.1 test report and see "VP Sheet" in this submission template.]
5.0 | Packaging
| Materials used for packaging the finished product are to be free of ozone-depleting compounds as defined in the Montreal Protocol. The general specification of shipping containers will be subject to agreement with the individual procurement agencies, but packaging in general should be strong export packaging able to withstand rough handling during transit. | [Please confirm all of the following: - Packaging materials are free of ozone-depleting compounds - The type of Packaging material that will provide adequate protection of the goods for carriage including adverse climatic and storage conditions and high humidity in accordance with the PQS clause requirement.]

## VP
E007 Submission to PQS for approval: Three-phase voltage stabilizer for AC powered Walk-In Cold & Freezer Rooms |  |  | Brand & Model:
| Compliance with PQS specification: | E007/VS02.1
| As shown by testing in accordance with PQS verification protocol: | E007/VS02-VP.1
Instructions in [square brackets] are for your guidance. Please delete these instructions and replace with evidence or a precise reference (including page and section numbers) showing compliance with that particular PQS specification requirement. In general a "pass" or "complies" statement alone is not acceptable.
One document may provide evidence for several clause requirements. Please carefully reference the sub-sections of any such document so that it is clear that the clause requirement has been met. This will help speed the pre-qualification process.
Greyed-out cells do not require a response.
NOTE: If it is not clear or doubtful whether a requirement has been met, then this is a non-compliance and pre-qualification might be delayed.
| Please also complete the Spec sheet. |  | REVIEWER’S SUMMARY: |  | REVIEWER’S SUMMARY: |  | REVIEWER’S SUMMARY:
Section 7. | VP Clause | Applicant's submission | Assessor's remarks [Name & Date] | Applicants response [Name & Date] | Assessor's remarks [Name & Date] | Applicants response [Name & Date] | Assessor's remarks [Name & Date]
5.1 | Evidence of conformity assessment
| Products must carry the CE mark, UL mark and/or equivalent internationally accepted evidence of conformity assessment. | [Please provide evidence of any conformity mark if the appliance has one.]
5.2 | Number of samples
| The legal manufacturer or reseller must complete a full Product Dossier to be supplied to the WHO IMD-PQS Secretariat in accordance with the manufacturer’s design specification. Each sample of the product shall be self-tested to validate performance. If the product is available in more than one version and with different voltage combinations as indicated in the table of specification Clause 4.2.2, test one sample of each version. Condition of samples: The legal manufacturer or reseller must test the sample in accordance with the final form to be supplied to the end-customer. | [Please provide the testing laboratory a draft dossier for checking and amendment. This will help to ensure that the dossier is complete.]
5.3 | Test procedure
Document and report test conditions (temperature, humidity, load, etc.) for each test.
5.3.1 | Voltage and frequency
The specific tests apply equally to each combination of stabilizer type and rated input/output voltage/frequency. Relevant input voltage/frequencies are given in the format: 120 V/50-60 Hz, 230 V/50-60 Hz and 220-240V/380-415 V/50-60 Hz. The input supply voltage must be regulated to ±1.0% of the nominal voltage used in all tests below.
5.3.2 | Test 1: Type examination
| The test report must clearly show that the requirements of each section and sub-section in the type examination are individually and clearly met. | [Please refer to the test report and see the specification sheet in this template where precise references to each clause is required.]
5.3.3 | Test 2: Endurance test | The information requested below can be shown in one downloaded data file or in several downloaded data files as applicable so that the evidence is convincing to the PQS reviewer. The submission to PQS can enhanced with annotated notes.
| Perform a fully loaded endurance test at the input voltage and frequency extremes of the operating range based on the device’s type. Report on test conditions and results. | [Please refer to the precise section in the test report showing the input voltage and frequency throughout the test (this can be graphical). A "pass" statement alone is not acceptable.]